## ELE LT Panels
VIJAYAPURA DISTRICT CENTRAL CO-OPERATIVE BANK LTD VIJAYAPUR
TRANING CENTER NON SR ITEMS OF FIRE FIGHTING WORKS
Sl No. | Description | Unit | Quantity | REMARKS
1 | 2 | 3 | 4 | 5
1 | LT ISOLATOR Panels (Outdoor Type)
Design, manufacturing, Supply, installation,testing and commissioning of floor mounting free standing totally enclosed outdoor IP-55 cubical extensible compartmentalized front operational, vertical, dust and vermin proof LT panels fabricated out of 2 mm thick CRCA sheet steel provided with hinged detachable lockable and front and back openable compartmentalized individual chamber doors including strengthening with suitable size angle iron frame work complete as required. The panel shall be powder coated.Cable entry / exit shall be from bottom only & Panel shall be placed over a platform structure.Nessary canopy to be provided as per requirement. Aslo refer the Schematic Diagram for feeder ratings.
Note : General for all panels 1. The fault withstanding capacity shall be for one sec. Earth bus shall be part of the panel.
2. All I/C and O/G breakers shall be provided with potential free contacts .
3. All O/G MCCB shall having O/C& S/C releases.
4. All I/C MCCB shall having O/C, S/C & EF releases with Shunt trip coil.Unless otherwise specified
5. MCCB Breaker upto & including 250A shall be with Thermal release and Above 250A shall be Microrocessor based release.
6.Bus bar sizing shall be based on the current density of 0.8A/Sqmm for Aluminum and 1A/Sqmm for Copper bus bars
A) | OUTDOOR, IP 55 , LT-ISOLATORS
i) | Incomings/Outgoing
a) | 1600A FP EDO ACB, 50 KA, breaking capacity with Microprocessor based OL & SC protections along with necessary CT's,
b) | Type -1+2 Surge Protection Device with Back up fuse and Tested as per IEC 61643 Part 11:2011,
c) | R,Y,B indication lamps along with back up MCB
d) | ON/OFF/Trip indicating lamps.
e) | Emergency Pushbuttons with Shunt trip coil
| LT ISOLATOR PANEL described as above | Nos | 1
2 | MAIN LT PANEL
Supply, installation,testing and commissioning of floor mounting free standing totally enclosed indoor duty, with IP 42 protection, cubical type front operational dust and vermin proof panel fabricated out of 2.0 mm thick CRCA sheet steel, powder coated provided with hinged detachable lockable , front and back openable compartmentalized individual chamber doors complete as required. The panel shall be mounted on suitable MS channels: (Refer Attached Single Line Diagram).
Mains Incomings -1 No.
a) | Automatic Transfer Switch ATyS g, switching type I-0-II, 4P 1600A
b) | 1600A FP EDO ACB, 50 KA, breaking capacity with Microprocessor based OL & SC protections along with necessary CT's,
c) | Type -1+2 Surge Protection Device with Back up fuse and Tested as per IEC 61643 Part 11:2011,
d) | R,Y,B indication lamps along with back up MCB
e) | ON/OFF/Trip indicating lamps.
f) | Emergency Pushbuttons with Shunt trip coil
g) | Digital type multifunction meter (MFM) with RS 485 PORT AND required CT's of ratio 1000/5A.CL-1, 10VA burden.
Bus Bar
Two Sets of 1600A, 50KA, FP Aluminium Bus Bars of suitable length. Bus bars shall be colour coded and insulated by heat shrinkable sleeves & clip on shrouds for joints. The bus bar sizing calculations shall be submitted for approval, after considering all derating factors.
Outgoings-Sectoin
All out goings MCCB's shall be provided with OL & SC, protection. All MCCB's shall be provided with RYB Indiaction lamps and ON/OFF & Trip indication lamps along with 2.5A MPCB protection.
a) | 2 Nos 800A, 36 KA,FP, MCCB with Microprocessor based OL & SC Releases. Each breaker shall have necessary CT's and Dual source reading energy meters
b) | 4 Nos 630A, 36 KA,FP, MCCB with Microprocessor based OL & SC Releases.Each breaker shall have necessary CT's and Dual source reading energy meters
c) | 5 Nos 250A, 36 KA,FP, MCCB with Microprocessor based OL & SC Releases.Each breaker shall have necessary CT's and Dual source reading energy meters
d) | 2 No 100A, 36 KA,FP, MCCB with Microprocessor based OL & SC Releases.Each breaker shall have necessary CT's and Dual source reading energy meters
| MAIN LT PANEL described as above and as per SCHEMATIC | No. | 1
3 | DG AMF CUM SYNCHRONISATION PANEL
Supply of floor mounting free standing totally enclosed indoor duty, with IP 42 protection, cubical type front operational dust and vermin proof DG Synchronisation panel fabricated out of 2.0 mm thick CRCA sheet steel, powder coated provided with hinged detachable lockable , front and back openable compartmentalized individual chamber doors complete as required. The panel shall be mounted on suitable MS channels: (Refer Attached Single Line Diagram).
a) | Incoming Breakers : 2 Nos. with followings
i) | 800A (500 KVA DG SET) motor operated spring charged Four pole, EDO, 36 kA, MCCB of drawout pattern arrangement for cable connection on incoming side and busbar connection on outgoing side. MCCB's shall be electrically and mechanically interlocked with bus coupler. The Microprocessor based Release as described below in protection section
This panel should include Type -2 Surge Protection Device with Back up HRC fuse Tested as per IEC 61643 Part 11:2011,
b) | Metering and Indication:
ii) | Each MCCB shall be provided with 1 No Digital type multifunction meter (MFM) with RS 485 PORT AND required CT's of ratio 1250/5A.CL-1, 10VA burden.
iii) | Each MCCB shall be provided with 1 No Counter type Energy meter with required CT's of ratio 1250/5A.CL-1, 10VA burden.
iv) | Each MCCB shall have 3 Nos. of phase indicating lamps, Breaker ON/OFF/TRIP / 'DC control supply healthy', and spring charged indicating lamps.
v) | Auxiliary contactor 6 NO + 6 NC, suitable for 24 V DC in each incomer breaker
a) | Control bus fitting with MCB.
b) | Neutral links.
c) | Hooter
d) | Indicating Lamps
e) | Set 'ON'
f) | Load on DG Set
g) | Load on main supply
h) | DG control supply healthy
i) | Auto Manual Switch
j) | T-N-C breaker control switch. (Trip / Neutral / Close).
b) | Protection for incoming MCCB's
Each MCCB shall be provided with required CT's of ratio 800/5A.CL-5P10, 10VA burden for following protections.
INCOMER MCCB shall HAVE FOLLOWING FEATURES OF RELAYS.
PROTECTION As Below
OVERCURRENT 40 % - 100 % - TIME SETTING
SELECTIVE SHORT CIRCUIT 60 % - 1000 % - TIME SETTING
INSTANTANEOUS SHORT CIRCUIT 150 % - 1500 %
EARTH FAULT WITH ADJUSTABLE RELAY 20 % - 100 %
Reverse Power relay
Under Voltage and Over voltage relay
Shunt trip release
Master trip relay, Trip circuit supervision relay
Over voltage/ undervoltage relay
Protections as specified above.
Required Nos.of Neutral CT's suitable for above DG sets
MANUAL SYNCHRONISATION
2 Nos. Auto / Manual switches
2 Nos.Dual Voltmeters
2 Nos.Dual Frequency meters
2 Nos.Dark Lamps
Required Nos of relays and contactors.
c) | 12 Window annunciation panel for following indication / Lamps
a) | Set fails to start.
b) | Engine overheat
c) | High Temperature.
d) | Low lube oil pressure.
e) | Over Speed
f) | Low Fuel oil level
g) | Cooling water Flow failure.
h) | Breaker Trip.
g) | Generator fault.
h) | DC control supply failure.
i) | Voltage out of limits.
j) | Spare.
(Neutral Bus Bar shall be fully rated)
Battery Charger
d) | Supplying, installing, testing and commissioning of 230 V, Single Phase, 50 HZ, AC operated Battery Charger for DC supply of following rating with Boost and trickle charging facility and protection from over charging the D.G. set starting battery and a DC DB with required numbers of outgoing DP MCB's plus 2 Nos. of 15 AMP. DP MCB's as spare feeders complete as required and as per specifications.
24 Volts 360 AH
e) | Bus Bars :
1 Set of 1600 Amps, 36KA FP 'AL' Bus bar of each section.
FP Aluminium Bus Bars of suitable length. Bus bars shall be colour coded and insulated by heat shrinkable sleeves & clip on shrouds for joints. The bus bar sizing calculations shall be submitted for approval, after considering all derating factors.
f) | Outgoing :
All outgoing feeders shall be provided with ON/OFF indicating lamps and 2.5A SP MPCB protection and Digital KWH of required range and CT's. All out goings MCCB's shall be provided with OL, SC, EF & Instantaneous protection. All MCCB's shall be provided with RYB Indiaction lamps and ON/OFF & Trip indication lamps.
a) | 1 No 1600 Amp FP, ACB of 36 kA breaking capacity with Energy meter and necessary CT's.
b) | 2 Nos 630 Amp FP, MCCB of 36 kA breaking capacity with Energy meter and necessary CT's.
g) | Protective devices
The outgoing ACB shall be provided with the following protective devices:-
i. | 230 Volt A.C. shunt trip coil.
ii. | Separate CT's shall be provided for protective system and measuring system.
iii. | Microprocessor based O/C, short circuit and earth fault protection release.
h) | PLC for auto mains failure, DG Synchronisation, auto load management, Auto load sharing & breaker interlocking as per logic specified. (Similar to EasyGen 3200 or equivalent)
i. | Auto start of DG sets on grid through under voltage & phase reversal relay.
ii. | Auto Load sharing and load balancing
iii. | Auto changeover of DG & Transformer incomers and interlcoking with buscouplers
iv. | Synchronisation of all 2 DG sets based on the demand.
iv. | Necessary hardware shall be provided to achieve above function including PLC with real time clock, digital input / output MMI with two line display, power supply, Auxiliary relays, push buttons, indicating lamps & software for the same etc. as required.
v. | Automatic system shall be user friendly & have manual override.
vi. | Any other requirement for the auto operation of system for load management, interlocking shall be considered as part of BOQ.
i) | MIMIC DIAGRAM
MIMIC shall be made of polycarbonate sheet of 5 mm thickness fixed on acrylic sheet of 2mm thick. the size of panel shall be such that the diagram can be visualized from 5 to 6 meter distance. The panel shall display complete single line diagram of DG Synchronisation Panel. This line diagram shall be made from luminous non fading materials to glow in dark and each breaker legend shall be provided with bi-colour LED lights to show the ON/OFF status of the respective feeder (Incomers / Bus couplers)
| DG AMF CUM SYNCHRONISATION PANEL, as described above, As per Schematic and as per specification complete in all respects. | Set | 1
4.0) | 345 KVAR APFCR PANEL
i) | Incoming
1 Nos. of 800 Amp FP MCCB of 16 KA breaking capacity With O/C, S/C,EF & Shunt trip release with interlocking facility.
This panel should include Type -2 Surge Protection Device with Back up HRC fuse Tested as per IEC 61643 Part 11:2011,
Earth Leakage Relay with Core Balance Current Transformer (CBCT) in incommer.
250A, 3 Phase Dual KWH meter & necessary 250A / 5A,CL 0.5,10VA CT's with sealing and locking arrangement.
R,Y,B indication lamps along with back up MCB
ON/OFF/Trip indicating lamps.
ii) | Bus Bar
A Set of 250 amp, 25kA TPN Aluminium Bus bar of suitable length.
iii) | Outgoing
Each outgoing MCCB should contain the followings:
R,Y,B indication lamps along with back up MCB
vi. | Stepped relay(APFCR) with 8 steps for automatic power factor correction.
vii. | 1 Nos of capacitor duty TP contactors of 250 amp.
3 Nos of capacitor duty TP contactors of 125 amp.
4 Nos of capacitor duty TP contactors of 63 amp.
viii. | 1 No. 100 KVAR MPP type 2mm thick capacitor banks and 7% detuned reactors..
4 Nos. 50 KVAR MPP type 2mm thick capacitor banks and 7% detuned reactors..
3 Nos. 15 KVAR MPP type 2mm thick capacitor banks and 7% detuned reactors..
ix | 1 Nos. 250A TP MCB of 25 KA service breaking capacity.
3 Nos. 125A TP MCB of 25 KA service breaking capacity.
4 Nos. 63A TP MCB of 25 KA service breaking capacity.
x | 10 Sets of Push button stations 'RED' and 'GREEN' push buttons for manual operation of capacitors.
xi | 1 No. selector switches for changing automatic to manual operation of capacitors.(A/M)
| 345 KVAR APFC Panel described as above & As per Schematic drawing. | Nos | 1
5.0) | FIRE EMERGENCY PANEL
i) | Incoming
1 Nos. 630 amp FP On load Manual Change over switch (Two incoming Supply, installation,testing and commissioning of from Main EB Supply, installation,testing and commissioning of, one working & one standby)
1 No. of 630 Amp FP MCCB of 25 KA breaking capacity With O/C, S/C,EF & Shunt trip release with interlocking facility.
This panel should include Type -2 Surge Protection Device with Back up HRC fuse Tested as per IEC 61643 Part 11:2011,
Earth Leakage Relay with Core Balance Current Transformer (CBCT) in incommer.
630A, 3 Phase Dual KWH meter & necessary 600A / 5A,CL:1,10VA CT's with sealing and locking arrangement.
R,Y,B indication lamps along with back up MCB
ON/OFF/Trip indicating lamps.
ii) | Bus Bar
A Set of 630 amp, 25kA TPN Aluminium Bus bar of suitable length.
iii) | Outgoing
Each outgoing should contain the followings:
R,Y,B indication lamps along with back up MCB
1 nos of 400 A TPN MCCB of 25KA breaking capacity.
1 nos of 250 A TPN MCCB of 25KA breaking capacity.
2 nos of 100 A TPN MCCB of 25KA breaking capacity.
5 nos of 63 A TPN MCCB of 16KA breaking capacity.
| FIRE EMERGENCY PANEL described as above & As per Schematic drawing. | Nos | 1
6.0) | UTILITY PANEL
i) | Incoming
1 Nos. of 250 Amp FP MCCB of 16 KA breaking capacity With O/C, S/C,EF & Shunt trip release with interlocking facility.
This panel should include Type -2 Surge Protection Device with Back up HRC fuse Tested as per IEC 61643 Part 11:2011,
Earth Leakage Relay with Core Balance Current Transformer (CBCT) in incommer.
250A, 3 Phase Dual KWH meter & necessary 250A / 5A,CL 0.5,10VA CT's with sealing and locking arrangement.
R,Y,B indication lamps along with back up MCB
ON/OFF/Trip indicating lamps.
ii) | Bus Bar
A Set of 250 amp, 25kA TPN Aluminium Bus bar of suitable length.
iii) | Outgoing
Each outgoing MCCB should contain the followings:
R,Y,B indication lamps along with back up MCB
i) | 12 nos of 63 A TPN MCB of 16 KA breaking capacity.
| Utility PANEL described as above & As per Schematic drawing. | Nos | 1
7.0) | END FEED UNITS FOR RISING MAINS
i) | Design fabrication Supply, installation,testing and commissioning of following end feed units fabricated out of 1.6 mm thick sheet steel powder coated enclosure and consisting of following rating MCCB's and Manual change over switch with Phase indication lamps and breaker status indication lamps
| 630A,36KA, TPN MCCB | Nos. | 1
8.0) | FLOOR LTG & RP PANEL
i) | Incoming
1 Nos. 160 amp FP On load Manual Change over switch (Two incoming Supply, installation,testing and commissioning of from Main EB Supply, installation,testing and commissioning of, one working & one standby)
1 Nos. of 160 Amp FP MCCB of 16 KA breaking capacity With O/C, S/C,EF & Shunt trip release with interlocking facility.
This panel should include Type -2 Surge Protection Device with Back up HRC fuse Tested as per IEC 61643 Part 11:2011,
Earth Leakage Relay with Core Balance Current Transformer (CBCT) in incommer.
160A, 3 Phase Dual KWH meter & necessary 250A / 5A,CL 0.5,10VA CT's with sealing and locking arrangement.
R,Y,B indication lamps along with back up MCB
ON/OFF/Trip indicating lamps.
ii) | Bus Bar
A Set of 160 amp, 25kA TPN Aluminium Bus bar of suitable length.
iii) | Outgoing
Each outgoing MCCB should contain the followings:
R,Y,B indication lamps along with back up MCB
i) | 12 nos of 63 A TPN MCB of 16 KA breaking capacity.
| FLOOR LTG & RP PANEL described as above & As per Schematic drawing. | Nos | 1
9.0) | 4TH FLOOR LTG & RP PANEL
i) | Incoming
1 Nos. 160 amp FP On load Manual Change over switch (Two incoming Supply, installation,testing and commissioning of from Main EB Supply, installation,testing and commissioning of, one working & one standby)
1 Nos. of 160 Amp FP MCCB of 16 KA breaking capacity With O/C, S/C,EF & Shunt trip release with interlocking facility.
This panel should include Type -2 Surge Protection Device with Back up HRC fuse Tested as per IEC 61643 Part 11:2011,
Earth Leakage Relay with Core Balance Current Transformer (CBCT) in incommer.
160A, 3 Phase Dual KWH meter & necessary 250A / 5A,CL 0.5,10VA CT's with sealing and locking arrangement.
R,Y,B indication lamps along with back up MCB
ON/OFF/Trip indicating lamps.
ii) | Bus Bar
A Set of 160 amp, 25kA TPN Aluminium Bus bar of suitable length.
iii) | Outgoing
Each outgoing MCCB should contain the followings:
R,Y,B indication lamps along with back up MCB
i) | 5 nos of 63 A TPN MCB of 16 KA breaking capacity.
ii) | 18 nos of 63 A DP MCB of 16 KA breaking capacity.
| 4TH FLOOR LTG & RP PANEL described as above & As per Schematic drawing. | Nos | 1
10.0) | CAR CHARGING PANEL
i) | Incoming
1 Nos. 250 amp FP On load Manual Change over switch (Two incoming Supply, installation,testing and commissioning of from Main EB Supply, installation,testing and commissioning of, one working & one standby)
1 Nos. of 250 Amp FP MCCB of 16 KA breaking capacity With O/C, S/C,EF & Shunt trip release with interlocking facility.
ii) | Protection, Meters & Indication for incoming
This panel should include Type -2 Surge Protection Device with Back up HRC fuse Tested as per IEC 61643 Part 11:2011,
Earth Leakage Relay with Core Balance Current Transformer (CBCT) in incommer.
250A, 3 Phase Dual KWH meter & necessary 250A / 5A,CL: 1, 10VA CT's with sealing and locking arrangement.
R,Y,B indication lamps along with back up MCB
ON/OFF/Trip indicating lamps.
iii) | Bus Bar
A Set of 250 amp, 16kA TPN Aluminium Bus bar of suitable length.
iv) | Outgoing
i) | 30 Nos 63A TPN MCB of 16 KA breaking capacity.
| CAR CHARGING Panel described as above & As per Schematic drawing. | Set | 1
11.0) | EMERGENCY LTG PANEL
i) | Incoming
1 Nos. 100 amp FP On load Manual Change over switch (Two incoming Supply, installation,testing and commissioning of from Main EB Supply, installation,testing and commissioning of, one working & one standby)
1 Nos. of 100 Amp FP MCCB of 16 KA breaking capacity With O/C, S/C,EF & Shunt trip release with interlocking facility.
ii) | Protection, Meters & Indication for incoming
This panel should include Type -2 Surge Protection Device with Back up HRC fuse Tested as per IEC 61643 Part 11:2011,
Earth Leakage Relay with Core Balance Current Transformer (CBCT) in incommer.
100A, 3 Phase Dual KWH meter & necessary 100A / 5A,CL: 1, 10VA CT's with sealing and locking arrangement.
R,Y,B indication lamps along with back up MCB
ON/OFF/Trip indicating lamps.
iii) | Bus Bar
A Set of 100 amp, 16kA TPN Aluminium Bus bar of suitable length.
iv) | Outgoing
i) | 10 Nos 63A TPN MCB of 16 KA breaking capacity.
| EMERGENCY LTG Panel described as above & As per Schematic drawing. | Set | 1
12) | EXTERNAL LIGHTING PANEL
Supply, installation,testing and commissioning of, installation, testing and commissioning of outdoor, double door type, front operated, front access, totally enclosed, free standing, dust and vermin proof feeder pillars with double door, IP-55ingress protection, fabricated from 2 mm thick CRCA sheets, with hinged, gasketted and lockable doors including the cost of interconnections, copper crimping lugs, brass glands, bonding to earth and painting, suitable for use at 415 volts, 3phase 4 wire 50Hz system with 15MVA rupturing capacity at 415 volts complete as per specifications and as below.
All live accessible parts shall be shrouded and all equipment shall be finger touch proof. The busbar insulation shall be with heat shrinkable sleeves. SMC/DMC shrouds and busbar supports shall be used. Padlocking facility and suitable MS frame with front cover sheet shall be provided.
a | Feeder Pillar
Incoming:
1 No. 63A 4 pole MCCB of 16 KA breaking capacity.
Incomer shall be provided with R,Y,B indication lamps along with back up MCB
MFM with 60/5A, class-1, 10 VA burden.CT's
Busbar
100 AMP 16 KA AL busbar of required length
Outgoings:
5 Sets 20 A, FP MCB’s with 6 Nos of 16A DP MCB's and 6 Nos. of DP Contactor with 6 Nos of 24 Hour Timer arranged in each phase
10 Nos. 40 A, DP MCB’s
| External lighting Feeder Pillar as described above and as per Schematic drawing. | Nos | 1

## ELECTRICLE OTHER
VIJAYAPUR DISTRICT CENTRAL COOPERATIVE BANK LTD VIJAYAPUR
TRAINING CENTRE ELECTRICAL OTHERS NON SR ITEM
SL NO | DESCRIPTION | UNIT | QTY | REMARKS
1 | 2 | 3 | 4 | 5
1 | BUSDUCTS AND ACCESSORIES (SANDWICH)
Supplying, installing on wall or suspension on ceiling , testing and commissioning of following capacity Air insulated Compact Type Bus trunking for the use on 3 Phase 4 wire 415Volts, 50HZ A>C.supply with metal clad enclosure having IP-54 rating after fixing the tap off boxes and all accessories, made of 1.6mm thick steel sheet duly powder coated in convenient sectionscomplete with 4 nos aluminium bus barshaving current density of 130A/sq.cm at nominal current rating, necessary joints,elbow joints& expansion joints, fire barrierat each floor, continuous earthing with 3 nosaluminium strip of suitable size(one on each side) including G>I clamping brackets, suspenders, angle iron bracket,steel fasteners,connecting to earthing
1.1 | 630A,Isc=36ka for 1 second(Page No.-16, DSR-2022 ; Item No. 3.9.6), Minimum 2 Nos of taping points shall be available in 3 Mtr straight length. Note: Need to consider 4nos of End cap also as required flanges | Mtr | 1
1.2 | Additional plug in hole | Nos | 1
1.3 | Flange | Nos | 1
1.4 | End cap | Nos | 1
1.5 | Fixed Support (1pc/set) | Set | 1
1.6 | Vertical Spring Hanger (1pc/set) | Set | 1
Supplying, istalling, testing and commissioning of following capacity TPN tap off box / Plug in box made of 1.mm thick sheet steel enclosure duly painted with powder coating on existing overhead bus bar systemcomplete with TPN disconnector FSU and HRC fuses, connections,earthing etc as required
1.7 | 160A | Nos | 1
1.8 | 250A | Nos | 1
1.1 | 1600A Outdoor type sandwich bus duct | Rm | 1
1.11 | 1600A Outdoor type sandwich bus duct 90deg Vertical / Horizonta bends | No | 1
1.12 | Obtuse angle bend (odd angle) 1600A Outdoor type sandwich bus duct | No | 1
1.13 | Termination of flexible at transformer/DG end with copper braided (TPN Set). 1600A Outdoor type sandwich bus duct | SET | 1
1.14 | Adapter chamber at DG/ transformer end 1600A Outdoor type sandwich bus duct | SET | 1
1.15 | End Flange Unit at transformer /DG/ switchgear end 1600A Outdoor type sandwich bus duct | No | 1
1.16 | Canopy for Busduct | No | 1
1.17 | Fabricating, supplying and fixing in position MS steel support system /supports/hangers/runners etc. for supporting the busducts including all cutting, welding, grinding, anchoring to RCC slabs/walls etc or erecting an independent MS structure to support the busduct in approved manner and as required and all incidental work complete | Kg | 1
NOTE: Any other related missing accessories item required for installation vendor shall be captured & mentioned while submitting the tender
SUB TOTAL FOR BUSDUCTS AND ACCESSORIES (SANDWICH)
2 | LIGHTENING PROTECTION
2.1 | Supply of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | Mtr | 1
2.2 | Polyamide Holder for fixing 8mm dia Conductor | Nos. | 1
2.3 | 16mm Dia Aluminium Air termination- 2000mm Long with 2 nos SS Clamp Suitable for side mounting on wall;Universal cross and T Connector -SS - for 16mm & 10 dia conductor | Set | 1
2.4 | Supply of SS Cross splicer suitable for 8mm dia. Conductor tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | Nos. | 1
2.5 | Supply of Expansion Piece without connector to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations to be provided on conductors length over 20 meters to connect Solid Round Al. Conductor at both ends to meet the requirements of IS/IEC 62305. | Nos. | 1
2.6 | Supply of Al. Straight Splicers for 8mm and 10 mm Conductor to meet the requirement of IS IEC 62305 tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | Nos. | 1
2.7 | Supply of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | Mtr | 1
2.8 | Polyamide Holder for fixing 8mm dia Conductor | Nos. | 1
2.9 | Each down-conductor should be provided with a test link in order to disconnect the earth termination system for enabling measurements. SS Test Link To connect Round to Flat conductor. | Nos. | 1
2.1 | Supply of Conductor Holder -SS for fixing 25 x 6 mm Strip | Nos. | 1
2.11 | Suply of 25 X 6 mm GI strip from AL Conductor to the earth pit station and further the same strip shall be used for interconnecting all the earth pits below ground leve Zinc coating: 500 g/m square (Approx :70 micron coating) Should be tested and use exclusively for lightning protection ,earthing system and ring equipotential bonding | Mtr | 1
2.12 | Supply of SS Cross splicer suitable for 25x6mm Strip . Conductor tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | Nos. | 1
2.13 | Supply & Installation of Corrosion Proof Band to meet the requirements of IS/IEC 62305. (For Covering Welding Joints) -100 mm width & 10 mtr long. | Nos. | 1
2.14 | Electrode CU Coated Steel Rods 14.2mm x 3000mm (250 M) UL;14.2 / OD SS Clamp Both Side;Jef Eco Safe carbon based backfill compound - 50 Pounds;"Eco Friendly rust proof heavy duty weather proof Polyethylene Earth Pit Chamber with following dimensions :240 mm dia (top), 317 mm dia (bottom) & 280 mm (height). | Set | 1
SUB TOTAL FOR LIGHTENING PROTECTION
3 | UPS & BATTERY SYSTEM
3.1 | Manufacture, assembly, supply, installation, testing, delivery and commissioning of 40KVA 3 phase input 3 phase output Conventional/Monolathic type Uninterruptible Power Supply (UPS) system. The individual UPS shall include a rectifier, an inverter, SNMP CARD - WEB ENABLED REMOTE MONITORING SYSTEM THROUGH INTERNET and such other peripherals required for paralleling the UPS system including parallel kit and static by pass switch.The quoted price shall also include MOD-BUS for BMS integration. Provision should be available for manual bypass also. The UPS systems offered shall be of the latest technology with Digital Control Microprocessor based, for reliable operation, using IGBT's in the inverter. The quality of design, manufacturing and inspection process should confirm to the relevant Inter-national standards such as IEC/EN/VDE. The operating efficiency of the UPS systems should be of the highest order while delivering quality power to the 100% non-linear loads. The UPS systems should be capable of communicating with the servers available with various users under various software / multiple platforms and also with BMS.The necessary harmonic LC filters shall be included. All complete as per relevant standards, technical specification. The rate should include fabricated MS frame Approximately 150mm height for bottom cable termination & the design shall ensure uniform distribution of weight.. | Nos | 1
3.2 | Supply, Installation, Testing and commissiong battery bank for 40KVA load. The battery should be of Conventional VRLA, 12V, FR container type, with end cell voltage of 1.7V of approved makes to give 15 minutes backup at full KVA load at Unity load power factor. The rate should include open type Racks & the design shall ensure uniform distribution of weight and DC MCCB, mP based, housed in Sheet steel enclosure made out of 14 SWG, duly powder coated complete with necessary spreders,shrouds , extended copper bus link,Battery terminal covering caps & hard wares suitable to terminate copper flexible cable. Antistatic sheet to be considered.The design shall ensure uniform distribution of weight.Battery bank should be double string design & each string should have MCCB Control. | Nos | 1
SUB TOTAL FOR UPS & BATTERY WORK
4 | DG SET Exhaust Piping System
4.1 | Supply & fixing of 10'' MS Class B Exhaust Pipe 4mm thick | RM | 1
4.2 | Supply & fixing of 10'' MS Exhaust Bend | Nos | 1
4.3 | Supply & fixing of 10'' Pipe Aluminium cladding ( Bend &Double Measurement) 26swg ,50mm tick glasswool | RM | 1
4.4 | Supply & fixing Silencer Aluminium Cladding | RM | 1
4.5 | Supply &fixing Pollucation testing Nozzle | Nos | 1
4.6 | Supply & Fixing of Dust collecting Nozzle | Nos | 1
4.7 | Supply & Fixing of 10'' SS Below with Flange & Fitting | Nos | 1

## PT SLAB WORKS
VIJAYAPURA DISTRICT CENTRAL CO-OPERATIVE BANK LTD VIJAYAPUR
TRANING CENTER NON SR ITEMS OF POST TENSION CONCRETE WORK
Sl No. | DESCRIPTION | UNIT | QTY | REMARKS
1 | 2 | 3 | 4 | 5
1 | POST TENSION CONCRETE WORK
A) Design Codes The design is in accordance with IS: 1343-1980, IS 456, BS8110: The Structural Use of Concrete, 1997 and TR43.
B) Pre - Stressing System & Materials  UPS Post-tensioning Bonded System.  Friction parameter:  = 0.2/rad, Wobble factor: K = 0.0017/m  Wedge draw-in = 6.0 mm a) Strand - 0.6” diameter 7-wire low relaxation non-coated bare strand to IS: 1343- 1980, IS 456, BS8110: The Structural Use of Concrete, 1997 and TR43 or relevant international codes. b) Anchorages - post-tensioning system, incorporating bonded, head &dead end anchorages. c) Sheathing - Galvanized steel strip ducting / HDPE Ducting d) Grout - Cementitious grout with additive. 28-day strength at 32 N/mm2 with maximum water cement ratio of 0.45.
C. Design Criteria a) Concrete = M45 N/mm2 / Steel Fe 500 b) Serviceability Classification = Post-tensioning Class 3 c) Fire rating = 2.0 hours d) Column Stiffness : M/bh2  4.0 N/mm2 Dimension : As per conforming to attached drawings e) Loading Conditions: All lateral loads are resisted by shear and core walls. f) PT option: PT Beam with PT Slab / PT Beams with RCC Slab : PT Slab : 225/350/265/200mm, PT Beam Size : 1200/1600/1400/1000/900/2000x700/500/750/600/550/1200/1400/1000/1500mm g) Design Loadings: LL: 5.0kN/Sqm; SDL: 2.5kN/Sqm
The PT Agency should have minimum 10 (Ten) years experience in post – tensioning works.
The PT Vendor Should Posses Design Experience & Execution Experience More than 10 Years in India.
The PT Systems (Anchorages) should be in use for more than 10 years and it should be validated by systems performance test conducted in a registered laboratory (IIT). a) Anchorage efficiency b) Load transfer test
PT agency should have the Proprietorship of their systems and their assembly.
Similar kind of PT Projects Completed in the last 3 years shall form part of the qualification.
Measurement shall be anchorage to anchorage + stressing length + profile length. (Cement/admixture/Reinforcement will be supplied by the Client/Main Contractor)
PT Beam and slab shall be designe for Live load 5 KN/Sq,m and Super imposed dead load of 2.5 KN/Sq.m.
1 | STILT FLOOR PT slab
GPTB-1 Size : 1200x700/500mm L : 40.390
GPTB-2 Size : 1200x700/500mm L : 40.480m
GPTB-3 Size : 1600x750mm L : 18.955m
GPTB-4 Size : 1200x600/750mm L: 9.920m
GPTB-5 Size :1400x550mm L : 14.150m
GPTB-6 Size : 1200x550mm L : 20.660m
GPTB-7 Size : 1200x550mm L : 20.970m
| GPTB-8&9 Size : 1400x550mm L : 14.150m | Job | 1
2 | GROUND FLOOR TPTB-1 & TPTB-2 Size : 1200x700mm L : 40.35m
TPTB-3 Size : 1200x700mm L : 19.96M
TPTB-3A Size : 1200x700mm L : 19.96M
TPTB-4 Size :1200x1000/700mm L : 40.145m
TPTB-5 Size :1200x1000/700mm L : 43.11
TPTB-6 & TPTB-7 Size : 900x700mm L : 19.96m
TPTB-8 Size : 1400x700mm L : 63.60
TPTB-9 Size : 1400x1000mm L : 30.955m
TPTB-10 & TPTB-11 Size:2200x1500/1000mm L : 34m
TPTB-12 & TPTB-13 Size: 1400x1000/700mm L : 27.75
| TPTB-14 Size : 1000x700mm L : 18.23m | Job | 1
3 | FIRST FLOOR TPTB-1 & TPTB-2 Size : 1200x700mm L : 40.35m
TPTB-3 Size : 1200x700mm L : 19.96M
TPTB-3A Size : 1200x700mm L : 19.96M
TPTB-4 Size :1200x1000/700mm L : 40.145m
TPTB-5 Size :1200x1000/700mm L : 43.11
TPTB-6 & TPTB-7 Size : 900x700mm L : 19.96m
TPTB-8 Size : 1400x700mm L : 63.60
TPTB-9 Size : 1400x1000mm L : 30.955m
TPTB-10 & TPTB-11 Size:2200x1500/1000mm L : 34m
TPTB-12 & TPTB-13 Size: 1400x1000/700mm L : 27.75
| TPTB-14 Size : 1000x700mm L : 18.23m | Job | 1
4 | SECOND FLOOR 3PTB-1 & 3PTB-2 Size : 1200x700mm L : 40.35m
3PTB-3 Size : 1200x700mm L : 19.96m
3PTB-4 Size :1200x1000/700mm L : 40.145m
3PTB-5 Size :1200x1000/700mm L : 43.11m
3PTB-6 & 3PTB-7 Size : 900x700mm L : 19.96m
3PTB-8 Size : 1400x700mm L : 63.60m
3PTB-9 Size : 1400x1000mm L : 30.955m
3PTB-10 & 3PTB-11 Size:2200x1500/1000mm L : 34m
3PTB-12 & 3PTB-13 Size: 1400x1000/700mm L : 27.75m
| TPTB-14 Size : 1000x700mm L : 18.23m | Job | 1

## FIRE WORKS
VIJAYAPURA DISTRICT CENTRAL CO-OPERATIVE BANK LTD VIJAYAPUR
TRANING CENTER NON SR ITEMS OF FIRE FIGHTING WORKS
Sl No. | Description | Unit | Quantity | REMARKS
1 | 2 | 3 | 4
1 | Supply, installation, testing and commissioning of 3 in 1 ( Hooter + MCP + P.A Speaker). | Each | 1
2 | Supply, installation, testing & commissioning of Beam Detector with base, junction box and other accessories as required and detectors shall be UL listed. | Each | 1
3 | Supplying, Installing, testing and commissioning flow switch installed on the sprinkler main distribution line connected to the main sprinkler annunciation panel. 25mm | Each | 1
4 | Supplying, Installing, testing and commissioning ICV. installed on the sprinkler main distribution line connected to the main sprinkler annunciation panel located in the ground floor. 150mm | Each | 1

## PHE WORKS
VIJAYAPURA DISTRICT CENTRAL CO-OPERATIVE BANK LTD VIJAYAPUR
TRANING CENTER NON SR ITEMS OF PLUMBING AND SANITARY WORKS
Sl No. | DESCRIPTION | UNIT | QTY | REMARKS
1 | 2 | 3 | 4 | 5
1 | Providing, fixing, testing and commissioning of PVC welded rain water head / khurras dome type grating with puddle flange to fix head in RCC slab specially fabricated from minimum 4mm thick PVC sheet, including removable heavy duty PVC grating of 50 x 3 mm thick PVC flats (Round or Square) as per approved design The quoted rate shall include for necessary grouting the khurras base with approved sealant complete all as shown in the drawing and as specified.
Rate Quoted shall be inclusive of cost of cement, sand and other consumables like hacksaw blade etc.
| 250 x 250mm PVC Grating | Nos | 1
Construction of percolation well / rain water recharge pit with precast RCC rings, coveringthe top with RCC slab including supply and fixing 600 x 600 RCC MH cover CI / MS rungs etc. The quoted rate shall include earth work excavation, back filling, removing excess earth and making good the floor. The percolation well harvest pit shall be constructed as per the detail drawings and specification shall conssit of:
a) | Allernate layers of brick bats, activated charcoal, gravel, pebbles and toped with fine sand for good infiltration.
b) | 1Nos. bore holes of 160 mm dia from the bottom of percolation pit for a depth of 6m, drilled by using auger manually.
c) | Bore hole to be filled with medium sized pebbles to provide meehamical strength to the holes and enhance infiltration.
d) | Rate quoted shall be inclusive of earthwosk excavation, back filling, removing of excess earth as per the instructions of engineer - in charge.
i) | Open well of 1.5m dia | Nos | 1
3 | Making of Core cutting in RCC Slab of all grade for Services as required etc.,including scaffolding etc., complete at all levels as per engineer in charge
For pipe dia
b) | 150mm to 200 mm dia | Nos | 1
4 | Providing and fixing of 600 x 600mm Heavy duty cast iron manhole cover with frame for Underground sump | Nos | 1
5 | FILTER FEED WATER PUMPS
Supplying, installing, testing and commissioning of 2 Nos. of Submersible type feed water pumps (One working + one stand by) for pumping the water from raw water U.G. sump through sand filter, activated carbon filter and antiscalent doser. The pump shall be coupled to adequate H.P. electrical motor, mounted on a common base frame made out of 'GI' with necessary bolts and nuts.The pump shall be provided with suitable enlosure with strainer arrangement for the protection of pumps.
The pump shall be suitable for the following requirements:
a) | Flow rate of each pump - 7.60 Cu.m / hr
b) | Head - 35-40 mtr.
The rate quoted shall be inclusive of:
a) | Suitable indoor wall mounting type control panel with auto / manual change - over switch including dry run protection arrangement, wiring upto panel, earthing for pumps and panel etc. complete.
b) | 1 no. pressure gauge 4" dial with needle valve and tee fittings.
c) | 3 nos. of Ball valves / Cast iron lever operated slim seal type butterfly valves of CI body (depend on the dia of pipe) and spheroidal graphite iron disc (SG iron), with nitrile rubber seal, tested to 10kg / sq.cm Confirming to BS 5155 / MF6 standards and including a set of GI flanges as per BS - 10 table1, including bolts, nuts, GI washers and neoprene rubber gaskets complete etc., (Inter valve / Audco make ) on the delivery side.
d) | 3 nos. slim seal flap type check valve with CI body and cast steel disc tested to PN - 10kg / sq.cm pressure including a set of GI flanges as per BS - 10 table1 including bolts, nuts, GI washers and neoprene rubber gaskets complete etc., (Inter valve / Audco make) on the delivery side.
e) | GI manifold of suitable dia on delivery side and suction side finished neatly with hot dip galvanizing to 100 microns with flanged end on either sides and collar provision for connectivity of above mentioned valves. | Set | 1
6 | Supplying, installing, testing and commissioning of 2 Nos. of Submersible type transfer pumps (1W + 1S) for pumping the water from Domestic water under ground sump to OHT. The pump shall be coupled to adequate H.P. electrical motor, mounted on a common base frame made out of 'GI' with necessary bolts and nuts..
The pump shall be suitable for the following requirements:
Flow rate of each pump - 7.60 Cu.m/Hr
Pump design head - 40-45 m
The pumps shall be provided with:
Suitable indoor wall mounting type control panel with auto / manual change - over switch including dry run protection arrangement, wiring upto panel, earthing etc. complete.
Industrial type electronic liquid level controllers with stainless steel probes / sensors or float switch for automatic operation.
| Alarm indication with signal in the event of pump failure etc. | Set | 1
7 | Supplying, installing, testing and commissioning of 2 Nos. of Submersible type transfer pumps (1W + 1S) for pumping the water from STP treated water under ground sump to OHT. The pump shall be coupled to adequate H.P. electrical motor, mounted on a common base frame made out of 'GI' with necessary bolts and nuts..
The pump shall be suitable for the following requirements:
Flow rate of each pump - 5.60 Cu.m/Hr
Pump design head - 50-55 m
The pumps shall be provided with:
Suitable indoor wall mounting type control panel with auto / manual change - over switch including dry run protection arrangement, wiring upto panel, earthing etc. complete.
Industrial type electronic liquid level controllers with stainless steel probes / sensors or float switch for automatic operation.
| Alarm indication with signal in the event of pump failure etc. | Set | 1
8 | Providing and fixing of PVC encappsulated foot steps 300 mm staggered apart for UG sump tank as per standard make of SFRC or equivalent make fixing in RCC walls during casting of RCC walls as per location shown in drawings. | Nos | 1
9 | Supply, installation, testing, commissioning of micro processor based LED type Auto level controller
| Auto –Manual Switch : To enable auto / manual operation of motor. | Set | 1
| Cable.including PVC conduit of required diameter | Mtr | 1
10 | Providing and fixing of MS brackets fabricated out of L angle / flats of required size with 6mm / 8mm GI `U' clamps with GI washers and nuts etc., for supporting GI MS sprinkler pipes running suspended in Ground floor and Basement floor ceiling level. The work shall also include making hole grouting the same in RCC slabs / masonry walls with cement concrete and making good the same. | Kg | 1
11 | SEWAGE TREATMENT PLANT CAPACITY - SBR - 115 KLD (EXCLUDING CIVIL WORKS) | L/s | 1
12 | WATER PRE TREATMENT PLANT - CAPACITY - 75 KLD
Sand pressure filters
Activated Carbon Filter
| Softeners and dosers | L/s | 1
13 | HEAT PUMP - CAPACITY - 1000 Ltrs. | L/s | 1

## Sheet1 (hidden)
SL NO | DESCRIPTION | UNIT | QTY | RATE IN INR |  | M/s D P ENGINEERING SOLUTIONS |  | M/s TECHMECH NM SOLUTION LLP |  | M/s ELESQUARE SYSTEMS |  | M/s OJUS POWER AND TECHNOLOGIES PVT. LTD. |  | M/s E POWER ENGINEERING |  | M/s E POWER ENGINEERING |  | M/s BUS CONNECT |  | M/s DELTA ELECTRONICS (INDIA) PVT. LTD. |  | M/s SINEPOWER TECHNOLOGIES |  | M/s AXIS ELECTRICAL COMPONENTS PVT. LTD. |  | M/s HYKON INDIA LTD.
|  |  |  | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
1 | BUSDUCTS AND ACCESSORIES (SANDWICH)
Supplying, installing on wall or suspension on ceiling , testing and commissioning of following capacity Air insulated Compact Type Bus trunking for the use on 3 Phase 4 wire 415Volts, 50HZ A>C.supply with metal clad enclosure having IP-54 rating after fixing the tap off boxes and all accessories, made of 1.6mm thick steel sheet duly powder coated in convenient sectionscomplete with 4 nos aluminium bus barshaving current density of 130A/sq.cm at nominal current rating, necessary joints,elbow joints& expansion joints, fire barrierat each floor, continuous earthing with 3 nosaluminium strip of suitable size(one on each side) including G>I clamping brackets, suspenders, angle iron bracket,steel fasteners,connecting to earthing
1.1 | 630A,Isc=36ka for 1 second(Page No.-16, DSR-2022 ; Item No. 3.9.6), Minimum 2 Nos of taping points shall be available in 3 Mtr straight length. Note: Need to consider 4nos of End cap also as required flanges | Mtr | 25 | 11540 | 2100 |  |  | 13300 | 2000 | 16273 | 2930 | [6 empty] | 11540 | 2100
1.2 | Additional plug in hole | Nos | 32 | 3213 |  |  |  | 3400 | 0 | 0 | 0 | [6 empty] | 3213
1.3 | Flange | Nos | 2 | 5458 | 2100 |  |  | 12000 | 7500 | 14956 | 2693 | [6 empty] | 5458 | 2100
1.4 | End cap | Nos | 2 | 2111 |  |  |  | 3500 | 0 | 10173 | 1832 | [6 empty] | 2111
1.5 | Fixed Support (1pc/set) | Set | 4 | 2111 |  |  |  | 2100 | 0 | 2789 | 503 | [6 empty] | 2111
1.6 | Vertical Spring Hanger (1pc/set) | Set | 24 | 2111 |  |  |  | 2100 | 500 | 279 | 51 | [6 empty] | 2111
Supplying, istalling, testing and commissioning of following capacity TPN tap off box / Plug in box made of 1.mm thick sheet steel enclosure duly painted with powder coating on existing overhead bus bar systemcomplete with TPN disconnector FSU and HRC fuses, connections,earthing etc as required
1.7 | 160A | Nos | 12 | 38948 | 1100 |  |  | 43000 | 1500 | 22727 | 4091 | [6 empty] | 38948 | 1100
1.8 | 250A | Nos | 2 | 44216 | 1100 |  |  | 47000 | 1500 | 45703 | 8227 | [6 empty] | 44216 | 1100
1.1 | 1600A Outdoor type sandwich bus duct | Rm | 5 | 20481 | 3400 |  |  | 22500 | 3800 | 95045 | 17109 | [6 empty] | 20481 | 3400
1.11 | 1600A Outdoor type sandwich bus duct 90deg Vertical / Horizonta bends | No | 2 | 7956 |  |  |  | 10200 | 0 | 8237 | 1483 | [6 empty] | 7956
1.12 | Obtuse angle bend (odd angle) 1600A Outdoor type sandwich bus duct | No | 1 | 11934 |  |  |  | 22000 | 0 | 8237 | 1483 | [6 empty] | 11934
1.13 | Termination of flexible at transformer/DG end with copper braided (TPN Set). 1600A Outdoor type sandwich bus duct | SET | 2 | 43750 | 4000 |  |  | 41000 | 7000 | 48698 | 8766 | [6 empty] | 43750 | 4000
1.14 | Adapter chamber at DG/ transformer end 1600A Outdoor type sandwich bus duct | SET | 2 | 10000 | 2200 |  |  | 40000 | 7000 | 18000 | 3240 | [6 empty] | 10000 | 2200
1.15 | End Flange Unit at transformer /DG/ switchgear end 1600A Outdoor type sandwich bus duct | No | 2 | 9928 | 4000 |  |  | 17200 | 7000 | 15356 | 2765 | [6 empty] | 9928 | 4000
1.16 | Canopy for Busduct | No | 5 | 3125 | 1500 |  |  | 5000 | 700 | 9000 | 1620 | [6 empty] | 3125 | 1500
1.17 | Fabricating, supplying and fixing in position MS steel support system /supports/hangers/runners etc. for supporting the busducts including all cutting, welding, grinding, anchoring to RCC slabs/walls etc or erecting an independent MS structure to support the busduct in approved manner and as required and all incidental work complete | Kg | 750 | 169 |  |  |  | 135 | 40 | 190 | 35 | [6 empty] | 169
NOTE: Any other related missing accessories item required for installation vendor shall be captured & mentioned while submitting the tender
SUB TOTAL FOR BUSDUCTS AND ACCESSORIES (SANDWICH)
2 | LIGHTENING PROTECTION
2.1 | Supply of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | Mtr | 400 | 116 | 30 | [10 empty] | 116 | [7 empty] | 105
2.2 | Polyamide Holder for fixing 8mm dia Conductor | Nos. | 350 | 18 | 15 | [10 empty] | 18 | [7 empty] | 55
2.3 | 16mm Dia Aluminium Air termination- 2000mm Long with 2 nos SS Clamp Suitable for side mounting on wall;Universal cross and T Connector -SS - for 16mm & 10 dia conductor | Set | 20 | 2036 | 300 | [10 empty] | 2036 | [7 empty] | 2500
2.4 | Supply of SS Cross splicer suitable for 8mm dia. Conductor tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | Nos. | 60 | 157 | 100 | [10 empty] | 157 | [7 empty] | 290
2.5 | Supply of Expansion Piece without connector to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations to be provided on conductors length over 20 meters to connect Solid Round Al. Conductor at both ends to meet the requirements of IS/IEC 62305. | Nos. | 20 | 61 | 30 | [10 empty] | 61 | [7 empty] | 325
2.6 | Supply of Al. Straight Splicers for 8mm and 10 mm Conductor to meet the requirement of IS IEC 62305 tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | Nos. | 40 | 200 | 100 | [10 empty] | 200
2.7 | Supply of 8 mm dia solid Aluminium Conductor tested as per IEC 62561- 2 conducted in the Govt. aggregated thirty party laboratory to meet the requirement of IS/ IEC 62305 | Mtr | 300 | 116 | 30 | [10 empty] | 116 | [7 empty] | 105
2.8 | Polyamide Holder for fixing 8mm dia Conductor | Nos. | 300 | 18 | 15 | [10 empty] | 18
2.9 | Each down-conductor should be provided with a test link in order to disconnect the earth termination system for enabling measurements. SS Test Link To connect Round to Flat conductor. | Nos. | 20 | 300 | 300 | [10 empty] | 300 | [7 empty] | 55
2.1 | Supply of Conductor Holder -SS for fixing 25 x 6 mm Strip | Nos. | 20 | 42 | 30 | [10 empty] | 42
2.11 | Suply of 25 X 6 mm GI strip from AL Conductor to the earth pit station and further the same strip shall be used for interconnecting all the earth pits below ground leve Zinc coating: 500 g/m square (Approx :70 micron coating) Should be tested and use exclusively for lightning protection ,earthing system and ring equipotential bonding | Mtr | 375 | 281 | 50 | [10 empty] | 281
2.12 | Supply of SS Cross splicer suitable for 25x6mm Strip . Conductor tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350μs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol | Nos. | 60 | 191 | 50 | [10 empty] | 191
2.13 | Supply & Installation of Corrosion Proof Band to meet the requirements of IS/IEC 62305. (For Covering Welding Joints) -100 mm width & 10 mtr long. | Nos. | 2 | 3100 | 200 | [10 empty] | 3100
2.14 | Electrode CU Coated Steel Rods 14.2mm x 3000mm (250 M) UL;14.2 / OD SS Clamp Both Side;Jef Eco Safe carbon based backfill compound - 50 Pounds;"Eco Friendly rust proof heavy duty weather proof Polyethylene Earth Pit Chamber with following dimensions :240 mm dia (top), 317 mm dia (bottom) & 280 mm (height). | Set | 20 | 5894 | [11 empty] | 5894
SUB TOTAL FOR LIGHTENING PROTECTION
3 | UPS & BATTERY SYSTEM
3.1 | Manufacture, assembly, supply, installation, testing, delivery and commissioning of 40KVA 3 phase input 3 phase output Conventional/Monolathic type Uninterruptible Power Supply (UPS) system. The individual UPS shall include a rectifier, an inverter, SNMP CARD - WEB ENABLED REMOTE MONITORING SYSTEM THROUGH INTERNET and such other peripherals required for paralleling the UPS system including parallel kit and static by pass switch.The quoted price shall also include MOD-BUS for BMS integration. Provision should be available for manual bypass also. The UPS systems offered shall be of the latest technology with Digital Control Microprocessor based, for reliable operation, using IGBT's in the inverter. The quality of design, manufacturing and inspection process should confirm to the relevant Inter-national standards such as IEC/EN/VDE. The operating efficiency of the UPS systems should be of the highest order while delivering quality power to the 100% non-linear loads. The UPS systems should be capable of communicating with the servers available with various users under various software / multiple platforms and also with BMS.The necessary harmonic LC filters shall be included. All complete as per relevant standards, technical specification. The rate should include fabricated MS frame Approximately 150mm height for bottom cable termination & the design shall ensure uniform distribution of weight.. | Nos | 1 | 340000 | 10000 | [8 empty] | 352752 | [5 empty] | 325000 |  | 340000 |  |  |  | 310307
3.2 | Supply, Installation, Testing and commissiong battery bank for 40KVA load. The battery should be of Conventional VRLA, 12V, FR container type, with end cell voltage of 1.7V of approved makes to give 15 minutes backup at full KVA load at Unity load power factor. The rate should include open type Racks & the design shall ensure uniform distribution of weight and DC MCCB, mP based, housed in Sheet steel enclosure made out of 14 SWG, duly powder coated complete with necessary spreders,shrouds , extended copper bus link,Battery terminal covering caps & hard wares suitable to terminate copper flexible cable. Antistatic sheet to be considered.The design shall ensure uniform distribution of weight.Battery bank should be double string design & each string should have MCCB Control. | Nos | 1 | 152000 | 15000 | [8 empty] | 165000 | [5 empty] | 254000 |  | 152000 |  |  |  | 360140
SUB TOTAL FOR UPS & BATTERY WORK
4 | DG SET Exhaust Piping System
4.1 | Supply & fixing of 10'' MS Class B Exhaust Pipe 4mm thick | RM | 50 | 4850 | 2200 | 5577 | 2530 |  |  |  |  | 4850 | 2200
4.2 | Supply & fixing of 10'' MS Exhaust Bend | Nos | 4 | 2500 | 1120 | 2875 | 1300 |  |  |  |  | 2500 | 1120
4.3 | Supply & fixing of 10'' Pipe Aluminium cladding ( Bend &Double Measurement) 26swg ,50mm tick glasswool | RM | 75 | 1600 | 950 | 1840 | 1100 |  |  |  |  | 1600 | 950
4.4 | Supply & fixing Silencer Aluminium Cladding | RM | 2 | 25000 | 6400 | 28750 | 7500 |  |  |  |  | 25000 | 6400
4.5 | Supply &fixing Pollucation testing Nozzle | Nos | 2 | 3850 | 1850 | 4427 | 2150 |  |  |  |  | 3850 | 1850
4.6 | Supply & Fixing of Dust collecting Nozzle | Nos | 2 | 1650 | 950 | 1897 | 1100 |  |  |  |  | 1650 | 950
4.7 | Supply & Fixing of 10'' SS Below with Flange & Fitting | Nos | 3 | 2350 | 650 | 2702 | 750 |  |  |  |  | 2350 | 650
SUB TOTAL FOR Exhaust Piping System
TOTAL AMOUNT
GRAND TOTAL AMOUNT